## Guide
How to fill in this workbook
Edit only the YELLOW cells, on the Settings and Feeders sheets. This Guide sheet is reference only - nothing here is read by the dashboard. Cells marked MUST SET need a real value from your cable datasheet, battery datasheet, or routing drawings; cells marked 'default OK' can stay as shipped while you set up. Save the file, commit inputs.xlsx to your repo, refresh the dashboard.
Legend: | MUST SET - enter a real value | default OK - can stay as shipped | yellow cell = you edit it
Parameter | What to enter | Fill? | Example / default
ARRANGEMENT
Strings per rack (k) | How many strings share one HV box. 1 = single-string, 2 = dual-string. The two strings in a rack share one feeder. | MUST SET | 2 (dual-string)
Packs in series per string | Number of battery packs wired in series to make one string. | MUST SET | 4
Cells in series per pack | From the pack name: 104S1P = 104 cells in series. | MUST SET | 104
Nominal cell voltage | Per-cell nominal voltage. Informational only - used to display string voltage so you can sanity-check it against the bus. | default OK | 3.2 (LFP)
OPERATING POINT
DC bus voltage | The real DC voltage across the parallel strings at the operating point you are analysing. | MUST SET | ~1331 V (416 cells x 3.2); use your design value
Current source mode | Type exactly 'power' or 'direct'. power = tool computes total current from PCS kW. direct = you type the total current. | check | power
PCS DC power | Total DC power for the whole container, in kW. Used in power mode. Total current = power / bus voltage. | MUST SET | your PCS rating, e.g. 1500
Operating current (total) | Total container DC current in amps. Used only in direct mode; ignore it in power mode. | default OK | 1000
CONDUCTOR RESISTANCE (biggest accuracy driver)
Resistance source | Type exactly 'datasheet' or 'calc'. datasheet = you give ohm/km. calc = tool computes from resistivity and area. | check | datasheet
Cable DC resistance | DC resistance of the UL3932 2/0 AWG cable in ohm/km, from the datasheet. | MUST SET | 0.26 is a placeholder - confirm
Datasheet reference temp | The temperature the ohm/km figure is quoted at (usually 20 C). | default OK | 20
Resistivity rho (20C) | Only used in calc mode. Copper ~0.0175 ohm.mm2/m. | default OK | 0.0175
Conductor cross-section | Only used in calc mode. 2/0 AWG ~67.43 mm2. | default OK | 67.43
Operating conductor temp | The real worst-case conductor temperature in service, in C. Resistance is corrected up to this temp (hotter = more resistance). | MUST SET | e.g. 45-90 depending on design
Temp coefficient alpha | Copper ~0.00393 per C. How much resistance rises per degree. | default OK | 0.00393
Parallel cables per pole | If you run more than one cable in parallel per + or - pole, enter that count. Usually 1. | default OK | 1
Return-conductor factor | 2 if the feeder length is the one-way run (current loops out on + and back on -, so loop = 2x length). 1 if your length already counts both poles. | check | 2
CONNECTOR & STRING INTERNALS (all per ONE string)
Connector resistance (each) | Contact resistance of one connector, in ohm. 0 ignores it for now. | default OK | 0 to start
Connectors in series per string | How many connectors a string's current passes through. | default OK | 0 to start
String internal resistance | DC internal resistance of ONE 4-pack string, in ohm (the battery's own DCIR + internal busbars), from the pack datasheet. | MUST SET | 0 = cable-only worst case; real value equalises strings
String internal cabling segments | Cable lengths INSIDE one string, comma-separated: HVBox->Pack1, each pack-to-pack hop, last Pack->HVBox. 4 packs = 5 numbers. | MUST SET | replace 1600,500,500,500,800 with real lengths
ACCEPTANCE LIMITS (drive the pass/fail warnings)
Cable ampacity (per pole) | Current one cable can safely carry, in amps, AFTER derating for the duct install method and ambient temperature. | MUST SET | 190 is a placeholder
Allowable feeder voltage drop | Your max acceptable feeder voltage drop, as % of bus voltage. | check | 1.0
Allowable current imbalance | Max acceptable string-to-string current spread, as %. | check | 15
Max routing length | Flags any feeder longer than this, in mm. | check | 9000
FEEDERS SHEET
Feeder length (mm) | On the Feeders sheet: real cable length from the Combine Cabinet to each rack's HV box. One row per rack (6 rows for Design 2). Add/delete rows to change the rack count. Keep the 'HV Box N' labels. | MUST SET | replace the placeholder lengths
Priority - the cells that actually move the results and must be real:
feeder lengths (Feeders sheet) - cable ohm/km - operating conductor temp - string internal resistance - string cabling segments - DC bus voltage + PCS power - cable ampacity. Everything else can ride on the defaults while you set up.
Tip: the two text cells (Current source mode, Resistance source) must be typed exactly - power/direct and datasheet/calc - or the tool falls back to defaults.

## Settings
BESS DC Cable Analysis - Inputs
Fill in the YELLOW cells only. See the Guide sheet for what each one means. Do not change the 'Key' column - the dashboard reads it. Feeder lengths are on the Feeders sheet.
Parameter | Value | Unit | Fill? | Key (do not edit) | Notes
— Arrangement —
Strings per rack (k) | 2 | count | MUST SET | stringsPerRack | 1 = single-string HV box, 2 = dual-string
Packs in series per string | 4 | count | MUST SET | packsPerString | sets string voltage & cabling hops
Cells in series per pack | 104 | count | MUST SET | cellsPerPack | 104 for a 104S1P pack
Nominal cell voltage | 3.2 | V | default OK | vCell | ~3.2 for LFP (informational)
— Operating point —
DC bus voltage | 1500 | V | MUST SET | Vbus | real voltage across the parallel strings
Current source mode | power | power/direct | check | curMode | 'power' uses PCS kW; 'direct' uses the current below
PCS DC power | 2500 | kW | MUST SET | Ppcs | total DC power; I_total = P / Vbus
Operating current (total) | 0 | A | default OK | Idirect | used only when mode = direct
— Conductor resistance —
Resistance source | datasheet | datasheet/calc | check | resMode | 'datasheet' uses ohm/km; 'calc' uses rho & area
Cable DC resistance | 0.2766 | ohm/km | MUST SET | Rkm | UL3932 2/0 AWG datasheet value
Datasheet reference temp | 20 | degC | default OK | Tref | temp the ohm/km value is quoted at
Resistivity rho (20C) | 0.0176 | ohm.mm2/m | default OK | rho | copper ~0.0175 (calc mode only)
Conductor cross-section | 67.43 | mm2 | default OK | area | 2/0 AWG ~67.43 (calc mode only)
Operating conductor temp | 65 | degC | MUST SET | Tcond | real worst-case conductor temp in service
Temp coefficient alpha | 0.00393 | 1/degC | default OK | alpha | copper ~0.00393
Parallel cables per pole | 1 | count | default OK | nPar | divides conductor resistance
Return-conductor factor | 2 | x | check | feederK | x2 counts + and - feeder as the loop
— Connector & string internals (per string) —
Connector resistance (each) | 0.0003 | ohm | default OK | Rc | per connector; 0 = ignore
Connectors in series per string | 2 | count | default OK | nC
String internal resistance | 0.08947 | ohm | MUST SET | Rpack | one string DCIR; 0 = cable-only worst case
String internal cabling segments | 1600,500,500,500,800 | mm (csv) | MUST SET | rackSegs | one string loop HVBox->P1->..->Pn->HVBox
— Acceptance limits —
Cable ampacity (per pole) | 215 | A | MUST SET | amp | after derating; checked vs feeder & string current
Allowable feeder voltage drop | 1 | % | check | vdLim | % of bus voltage
Allowable current imbalance | 15 | % | check | imbLim | (Max-Min)/Average
Max routing length | 7000 | mm | check | lenLim | flags any feeder longer than this

## Feeders
Feeder lengths - Combine Cabinet to HV Box (one row per rack)
Edit the YELLOW lengths. Add or delete rows to change the rack count. Keep the 'HV Box N' labels in column A. These are PLACEHOLDERS - replace with your real routing schedule.
Fill? | MUST SET
HV Box | Feeder length (mm) | Notes
HV Box 1 | 2100
HV Box 2 | 3000
HV Box 3 | 3900
HV Box 4 | 4700
HV Box 5 | 5800
HV Box 6 | 6600